## Managers Report (Master)
Woodmen Hills Metro District Water/Wastewater Dept.
Managers Report For May 2019
4/24/19-5/20/19
Prepared by Jerry Jacobson
Total
Mains Cleaned 0 linear feet 15,123 linear feet
Mains Inspected 0 linear feet 5,639 linear feet
Lift Stations Monthly maintenance.
WHRWRF DO probe problem remedied allowing plant to run in Auto. Textiles are causing excessive
maintenance as check valves are cleaned at least weekly. Different check valves are
being investigated that might not foul as easily. Mixer had problems, swapped with on the
shelf unit which also had problems. Took a mixer out of an unused basin, both of the other
mixers are in Denver being serviced under warranty. Cells 2 and 4 were filled with water to
control odors. DMR-QA Study 39 underway.
Water Fire hydrant maintenance at 20%. Filter Plant 3 and Guthrie SCADA communication
problems are being addressed. DMC, Inc. will visit site in order to determine what needs
to be done to achieve full automation. Goal is to have full automation by peak demand
season. LFH6 is equipped and is being flushed prior to going on line. Backflow report
is complete, no violations. CCR is complete. There is a leak on Pine Valley Circle. A
leak detection firm was employed to pinpoint leak. Work is scheduled for May 29th. This
will be a significant repair causing many homes to be out of water. All homes affected will
be notified.
Comments: Work has begun on Lift Station One. WHMD staff are operating FHMD water system.
Wastewater staff has moved out of the District Office into the RWRF. Vac Truck and
CCTV Trailer are now at the RWRF as well.